## 40 CFR 60 IIII
40 CFR 60 Subpart IIII -- Standards of Performance for Stationary Compression Ignition Internal Combustion Engines
Applicability: | Manufacturers of stationary CI ICE with a displacement of less than 30 L per cylinder where the model year is 2007 or later for engines that are not fire pump engines.
Manufacturers of stationary CI ICE with a displacement of less than 30 L per cylinder where the model year is listed in Table 3 to this subpart or later model year, for fire pump engines.
Owners and operators of stationary CI ICE that commence construction after July 11, 2005 where the engines are manufactured after April 1, 2006 and are not fire pump engines, or fire pump engines manufactured after July 1, 2006 that are certified by the National Fire Protection Association.
Owners and operators of any stationary CI ICE that are modified or reconstructed after July 11, 2005 and any person that modifies or reconstructs any stationary CI ICE after July 11, 2005.
Owners and operators of stationary CI ICE that commence construction after July 11, 2005 are subject to the provisions of §60.4208.
Exemptions: | Stationary CI ICE being tested at a stationary CI ICE test cell/stand.
| Owners and operators of an area source subject to this subpart are exempt from the obligation to obtain a permit under 40 CFR Part 70 or 40 CFR Part 71 provided they are not required to obtain a permit under 40 CFR 70.3(a) or 40 CFR 71.3(a). They must still comply with the provisions of this subpart applicable to area sources. |  |  |  | 40 CFR 70.3(a)
40 CFR 71.3(a)
| Stationary CI ICE may be exempted under 40 CFR Part 1068, Subpart C; 40 CFR Part 89, Subpart J; or 40 CFR Part 94, Subpart J. |  |  |  | 40 CFR 1068, Subpart C
40 CFR 89, Subpart J
40 CFR 94, Subpart J
Owners and operators of facilities with CI ICE that are acting as temporary replacement units and that are located at a stationary source for less than 1 year and that have been properly certified as meeting the standards that would be applicable to each engine under the appropriate nonroad engine provisions are not required to meet any other provisions under this subpart.
General Standards for Manufacturers: | Stationary, Non-Emergency |  |  | Chart 1
| Stationary, Emergency, Non-Fire Pumps |  |  | Chart 2
| Fire Pumps beginning with the model years in |  | Table 3 | Table 4
Exemptions from General Standards for Manufacturers: | Stationary, Emergency and Non-Emergency | Areas of Alaska not accessible by the Federal Aid Highway System. |  | Engines may be certified to the standards of 40 CFR 94 or 40 CFR 1042, if Table 1 to 40 CFR 1042.1 identifies 40 CFR 1042 to be applicable and the engines will be used solely in either or both of the locations shown. | 40 CFR 94
|  | Marine offshore installations. |  |  | 40 CFR 1042
Engines reconstructed by manufacturers, although they may elect to do so.
General Standards for Owners and Operators: | Stationary, Non-Emergency |  |  | Chart 3
| Stationary, Emergency, Non-Fire Pumps |  |  | Chart 4
| Fire Pumps |  |  | Table 4
After December 31, 2008, owners and operators may not install stationary CI ICE (excluding fire pump engines) that do not meet the applicable requirements for 2007 model year engines.
After December 31, 2009, owners and operators may not install stationary CI ICE with a maximum engine power ≥ 19 kW (25 HP) (excluding fire pump engines) that do not meet the applicable requirements for 2008 model year engines.
After December 31, 2012, owners and operators may not install non-emergency stationary CI ICE with a maximum engine power ≥ 130 kW (175 HP) that do not meet the applicable requirements for 2011 model year non-emergency engines.
After December 31, 2013, owners and operators may not install non-emergency stationary CI ICE with a maximum engine power ≥ 56 kW (75 HP) and < 130 kW (175 HP) that do not meet the applicable requirements for 2012 model year non-emergency engines.
After December 31, 2014, owners and operators may not install non-emergency stationary CI ICE with a maximum engine power ≥ 19 kW (25 HP) and < 56 kW (75 HP) that do not meet the applicable requirements for 2013 model year non-emergency engines.
After December 31, 2016, owners and operators may not install non-emergency stationary CI ICE with a maximum engine power ≥ 560 kW (750 HP) that do not meet the applicable requirements for 2015 model year non-emergency engines.
After December 31, 2018, owners and operators may not install non-emergency stationary CI ICE with a maximum engine power ≥ 600 kW (804 HP) and < 2,000 kW (2,680 HP) and a displacement of ≥ 10 L per cylinder and < 30 L per cylinder that do not meet the applicable requirements for 2017 model year non-emergency engines.
It is prohibited to import stationary CI ICE with a displacement < 30 L per cylinder that do not meet the applicable requirements above afer the dates specified.

## Table 1
Maximum Engine Power | Emission standards for stationary pre-2007 model year engines with a displacement of <10 liters per cylinder and 2007-2010 model year engines >2,237 KW (3,000 HP) and with a displacement of <10 liters per cylinder in g/KW-hr (g/HP-hr)
| NMHC + NOX | HC | NOX | CO | PM
KW<8 (HP<11) | 10.5 (7.8) |  |  | 8.0 (6.0) | 1.0 (0.75)
8≤KW<19 (11≤HP<25) | 9.5 (7.1) |  |  | 6.6 (4.9) | 0.80 (0.60)
19≤KW<37 (25≤HP<50) | 9.5 (7.1) |  |  | 5.5 (4.1) | 0.80 (0.60)
37≤KW<56 (50≤HP<75) |  |  | 9.2 (6.9)
56≤KW<75 (75≤HP<100) |  |  | 9.2 (6.9)
75≤KW<130 (100≤HP<175) |  |  | 9.2 (6.9)
130≤KW<225 (175≤HP<300) |  | 1.3 (1.0) | 9.2 (6.9) | 11.4 (8.5) | 0.54 (0.40)
225≤KW<450 (300≤HP<600) |  | 1.3 (1.0) | 9.2 (6.9) | 11.4 (8.5) | 0.54 (0.40)
450≤KW≤560 (600≤HP≤750) |  | 1.3 (1.0) | 9.2 (6.9) | 11.4 (8.5) | 0.54 (0.40)
KW>560 (HP>750) |  | 1.3 (1.0) | 9.2 (6.9) | 11.4 (8.5) | 0.54 (0.40)

## Table 2
Engine power | Emission standards for 2008 model year and later emergency stationary CI ICE <37 KW (50 HP) with a displacement of <10 liters per cylinder in g/KW-hr (g/HP-hr)
| Model year(s) | NOX + NMHC | CO | PM
KW<8 (HP<11) | 2008+ | 7.5 (5.6) | 8.0 (6.0) | 0.40 (0.30)
8≤KW<19 (11≤HP<25) | 2008+ | 7.5 (5.6) | 6.6 (4.9) | 0.40 (0.30)
19≤KW<37 (25≤HP<50) | 2008+ | 7.5 (5.6) | 5.5 (4.1) | 0.30 (0.22)

## Table 3
Engine power | Starting model year engine manufacturers must certify new stationary fire pump engines according to § 60.4202(d)1
KW<75 (HP<100) | 2011
75≤KW<130 (100≤HP<175) | 2010
130≤KW≤560 (175≤HP≤750) | 2009
KW>560 (HP>750) | 2008
1 Manufacturers of fire pump stationary CI ICE with a maximum engine power greater than or equal to 37 kW (50 HP) and less than 450 KW (600 HP) and a rated speed of greater than 2,650 revolutions per minute (rpm) are not required to certify such engines until three model years following the model year indicated in this Table 3 for engines in the applicable engine power category.

## Table 4
Maximum engine power | Model year(s) | NMHC + NOX | CO | PM
KW<8 (HP<11) | 2010 and earlier | 10.5 (7.8) | 8.0 (6.0) | 1.0 (0.75)
| 2011+ | 7.5 (5.6) |  | 0.40 (0.30)
8≤KW<19 (11≤HP<25) | 2010 and earlier | 9.5 (7.1) | 6.6 (4.9) | 0.80 (0.60)
| 2011+ | 7.5 (5.6) |  | 0.40 (0.30)
19≤KW<37 (25≤HP<50) | 2010 and earlier | 9.5 (7.1) | 5.5 (4.1) | 0.80 (0.60)
| 2011+ | 7.5 (5.6) |  | 0.30 (0.22)
37≤KW<56 (50≤HP<75) | 2010 and earlier | 10.5 (7.8) | 5.0 (3.7) | 0.80 (0.60)
| 2011+1 | 4.7 (3.5) |  | 0.40 (0.30)
56≤KW<75 (75≤HP<100) | 2010 and earlier | 10.5 (7.8) | 5.0 (3.7) | 0.80 (0.60)
| 2011+1 | 4.7 (3.5) |  | 0.40 (0.30)
75≤KW<130 (100≤HP<175) | 2009 and earlier | 10.5 (7.8) | 5.0 (3.7) | 0.80 (0.60)
| 2010+2 | 4.0 (3.0) |  | 0.30 (0.22)
130≤KW<225 (175≤HP<300) | 2008 and earlier | 10.5 (7.8) | 3.5 (2.6) | 0.54 (0.40)
| 2009+3 | 4.0 (3.0) |  | 0.20 (0.15)
225≤KW<450 (300≤HP<600) | 2008 and earlier | 10.5 (7.8) | 3.5 (2.6) | 0.54 (0.40)
| 2009+3 | 4.0 (3.0) |  | 0.20 (0.15)
450≤KW≤560 (600≤HP≤750) | 2008 and earlier | 10.5 (7.8) | 3.5 (2.6) | 0.54 (0.40)
| 2009+ | 4.0 (3.0) |  | 0.20 (0.15)
KW>560 (HP>750) | 2007 and earlier | 10.5 (7.8) | 3.5 (2.6) | 0.54 (0.40)
| 2008+ | 6.4 (4.8) |  | 0.20 (0.15)
1 For model years 2011-2013, manufacturers, owners and operators of fire pump stationary CI ICE in this engine power category with a rated speed of greater than 2,650 revolutions per minute (rpm) may comply with the emission limitations for 2010 model year engines.
2 For model years 2010-2012, manufacturers, owners and operators of fire pump stationary CI ICE in this engine power category with a rated speed of greater than 2,650 rpm may comply with the emission limitations for 2009 model year engines.
3 In model years 2009-2011, manufacturers of fire pump stationary CI ICE in this engine power category with a rated speed of greater than 2,650 rpm may comply with the emission limitations for 2008 model year engines.

## Chart 1
Displacement per Cylinder (D) | < 10 L |  | 10 L ≤ D < 15 L |  | 15 L ≤ D < 30 L
Engine Power (P) | ≤ 3,000 HP | > 3,000 HP | < 4,985 HP | ≥ 4,895 HP
| ≤ 2,237 kW | > 2,237 kW | < 3,700 kW | ≥ 3,700 kW
Model Year
2007 | §§ 89.112, 89.113 | Table 1 | § 94.8 |  | § 94.8
2008
2009
2010 | 1039.101, 1039.102, 1039.104, 1039.105, 1039.107, & 1039.115
2011 |  | §§ 1039.101, 1039.102, 1039.104, 1039.105, 1039.107, & 1039.115
2012
2013 |  |  | §§ 1042.101, 1042.107, 1042.110, 1042.115, 1042.120, & 1042.145 | § 94.8 | § 94.8
2014 |  |  | §§ 1042.101, 1042.107, 1042.110, 1042.115, 1042.120, & 1042.145 |  | §§ 1042.101, 1042.107, 1042.110, 1042.115, 1042.120, & 1042.145

## Chart 2
Displacement per Cylinder (D) | < 10 L |  |  | 10 L ≤ D < 15 L |  | 15 L ≤ D < 30 L
Engine Power (P) | < 50 HP | 50 HP ≤ P ≤ 3,000 HP | > 3,000 HP | < 4,985 HP | ≥ 4,895 HP | < 2,682 HP | ≥ 2,682 HP
| < 37 kW | 37 kW ≤ P ≤ 2,237 kW | > 2,237 kW | < 3,700 kW | ≥ 3,700 kW | < 2,000 kW | ≥ 2,000 kW
Model Year
2007 | §§ 89.112 & 89.113 | §§ 89.112, 89.113, | Table 1 | § 94.8 |  | § 94.8
2008 | §§ 1039.104, 1039.105, 1039.107, 1039.115,
2009
2010
2011 |  | & §§ 1039.102 | §§ 89.112, 89.113,
2012
2013 | & Table 2 |  | & §§ 1039.102 | §§ 1042.101, 1042.107, 1042.115, 1042.120, & 1042.145 | § 94.8
2014 | [5 empty] | §§ 1042.101, 1042.107, 1042.115, 1042.120, & 1042.145 | § 94.8

## Chart 3
Displacement per Cylinder (D) | < 10 L | 10 L ≤ D < 30 L |  | > 30 L
|  |  | Pollutant | NOX |  |  | PM
|  |  | RPM (n) | < 130 | 130 ≤ n < 2,000 | ≥ 2,000
Model Year |  |  | Installation Date
pre-2007 | Table 1 | § 94.8(a)(1) | pre-2007 | 17.0 g/kW-hr (12.7 g/HP-hr) | 45∙n-0.2 g/kW-hr (34∙n-0.2 g/HP-hr) | 9.8 g/kW-hr (7.3 g/HP-hr) | 0.15 g/kW-hr (0.11 g/HP-hr) or reduce PM emissions by 60% or more
2007 | Chart 1 | Chart 1 | 2007
2008 |  |  | 2008
2009 |  |  | 2009
2010 |  |  | 2010
2011 |  |  | 2011
2012 |  |  | 2012 | 14.4 g/kW-hr (10.7 g/HP-hr) | 44∙n-0.23 g/kW-hr (33∙n-0.23 g/HP-hr) | 7.7 g/kW-hr (5.7 g/HP-hr)
2013 |  |  | 2013
2014 |  |  | 2014
2015 |  |  | 2015
2016 |  |  | 2016 | 3.4 g/kW-hr (2.5 g/HP-hr) | 9.0∙n-0.2 g/kW-hr (6.7∙n-0.2 g/HP-hr) | 2.0 g/kW-hr (1.5 g/HP-hr)

## Chart 4
Displacement per Cylinder (D) | < 10 L | 10 L ≤ D < 30 L |  | > 30 L
|  |  | Pollutant | NOX |  |  | PM
|  |  | RPM (n) | < 130 | 130 ≤ n < 2,000 | ≥ 2,000
Model Year |  |  | Installation Date
pre-2007 | Table 1 | § 94.8(a)(1) | pre-2007 | 17.0 g/kW-hr (12.7 g/HP-hr) | 45∙n-0.2 g/kW-hr (34∙n-0.2 g/HP-hr) | 9.8 g/kW-hr (7.3 g/HP-hr) | 0.40 g/kW-hr (0.30 g/HP-hr)
2007 | Chart 2 | Chart 2 | 2007
2008 |  |  | 2008
2009 |  |  | 2009
2010 |  |  | 2010
2011 |  |  | 2011
2012 |  |  | 2012 | 14.4 g/kW-hr (10.7 g/HP-hr) | 44∙n-0.23 g/kW-hr (33∙n-0.23 g/HP-hr) | 7.7 g/kW-hr (5.7 g/HP-hr)
2013 |  |  | 2013
2014 |  |  | 2014